Generic Specification For High Performance Power Monitoring, Revenue Metering, Power Quality Recording, and RTU Functionality

### Nexus® 1252 Meter

2.	PRODUCT

2.1	Power Meters

- Power meter shall be multi-function 3 phase solid state unit with ability to connect to either 3 phase, 4 wire Wye or 3 phase, 3 wire delta circuits.

- Power meter shall include two 10-character, alphanumeric passwords, which shall protect the unit from unauthorized tampering.

C.  Voltage and current inputs to the meter shall conform to the following at a minimum:

1.	Monitor shall accept input of four (4) independent voltage inputs and four (4) independent current inputs of the stated capacity.

2.	Voltage input shall be 120 volts AC with available option for direct connection to voltage circuits of up to 600 V AC without the use of potential transformers.

3.	Voltage input shall be optically isolated to 2500 volts DC. Shall meet or exceed ANSI C37.90.1 (Surge Withstand Capability)

4.	Current input shall be rated for 5 Amps with inputs 2x continuous programmable to any CT range.

5.	Current inputs shall be solid U-Bolt stud inputs with a ten-second over-current rating of 100 Amps, a three second over-current rating of 300 Amps, and a one-second over-current rating of 500 Amps; at 23 oC.

D.  Power meter shall measure and report the following quantities at a minimum:

1.	Voltage, both phase to neutral and phase to phase, for all three phases; Auxiliary voltage; Phase angles for each voltage relative to each other. One cycle, 200 milliseconds and one second readings shall be available simultaneously.

- Current, phase A, B, C, N-measured, and N-calculated; Phase angles for 	each current relative to voltages. One cycle, 200 milliseconds and one	second readings shall be available simultaneously.

3.	Watts (total and per phase), VARs (total and per phase), VA (total and per phase), Power Factor (total and per phase) and Frequency. 200 milliseconds and one second readings shall be available simultaneously.

4.	Accumulated Watt-hr, VA-hr, and VAR-hr; Watt-hr received; Watt-hr delivered. VAR-hr and VA-hr reading shall be stored in each of the 4 quadrants of power.

5.	Power demand shall be calculated using four (4) different averaging methods: Thermal Average, Block Window Average, Rolling Window Average, and Predicted Average. Values for all averaging intervals must be available simultaneously.

6.	Power meter shall provide updates of all voltage and current readings at intervals of 1 cycle, 200 milliseconds, and 1 second. Readings shall be available for both metering and control. All specified readings shall be made available via the RS485 ports.

7.	Power meter shall provide time-stamped maximum and minimum readings for every measured parameter.

8.	Power meter shall provide coincident VAR readings for all maximum Watt readings.

E.   Power meter shall provide the following accuracies:

1.	Voltage accuracy shall be within less than 0.05% for the 1 second readings and less than 0.1% for the 200 millisecond readings.

2.	Current accuracy shall be within less than 0.025% for the 1 second readings and less than 0.10% for the 200 millisecond readings.

3.	Power and energy accuracy shall be within less than 0.06% at unity PF and within 0.10% at 0.50 PF.

4.	Frequency accuracy shall be within less than 0.01 Hz for the 1 second 	readings and less than 0.03 Hz for the 200 millisecond reading.

- The unit shall have an auto-calibration circuit designed to calibrate the readings using an internal reference.  The calibration shall commence upon temperature change.

F.  Auto-calibration components:

- 8 Channel sample/hold, for each at the voltage and current channels.

- Precision internal references with real-time auto calibration for voltage 	and current channels.

- The voltage inputs shall be optically isolated to 2500 volts.

- Dual 16 bit A/D converters.

G.	Power meter shall provide multiple digital communication ports and support multiple open protocols.

1.	Meter shall include four (4) independent, digital communication ports. Each port shall be RS485 architecture. Port 1 shall be user selectable as either RS232 or RS485 architecture.

2.	Each port shall be user configurable with regard to speed, protocol, address, and other communications parameters. All ports shall support a maximum communication speed of 115k baud simultaneously.

3.	Meter shall have an Ethernet port as an available option.

a. Ethernet option shall enable Total Web Solutions (TWS) feature, which 	is a fully customizable Web server.

b. TWS shall use XML to provide access to meter’s real time data through 	Internet Explorer.

c. TWS shall allow 12 simultaneous sockets of TCP/IP to the meter.

d. TWS shall be configurable to enable email alarm notification to up to 	nine recipients.

4.	Meter shall have an internal modem as an available option.

  - Meter shall offer both Modbus and DNP 3.0 level 2 plus, open protocols as standard configurations. All instantaneous data, logged data, event data, power quality analysis and waveform information shall be available using these open protocols.

- Up to 136 measurements shall be able to be mapped to DNP Static points in the customizable DNP Point map.

- Up to 16 relays and 8 resets shall be controlled through DNP.

- Meter shall be able to hold 250 events of combinations, of four events that are shall be binary input change, frozen counter, counter change, analog change.

- Flexible combinations of 4 events such as binary input change, frozen counter, counter change, and analog change shall be available for up to 250 events.

- Meter shall allow freeze commands.

- Third party certification shall be available.

I.	Power meter shall enable users to perform Flicker analysis according to IEC61000-4-15.

- The unit shall provide users with logging and monitoring for instantaneous short term readings (PST-10min) and long term readings (PLT-4 hour).

- The meter shall be able to log Flicker readings.

- Flicker shall be available for both 50 Hz and 60 Hz systems.

- The Flicker algorithm shall support both 120 and 220 volts power systems.

J.	Meter shall be capable of recording time-stamped Flicker readings in an EN50160 log.

1.	Log shall be viewable through a Log Viewer application.

a.	EN50160 readings shall be viewable in chart format or displayed values 			format.

b.	Log shall be downloadable from Log Viewer application.

c.	Log shall be printable from Log Viewer application.

K.	The ability to view interharmonics, the discrete frequencies that lie between the harmonics of the power frequency voltage and current, shall be available.

- Frequencies shall be able to be observed, which are not an integer multiple of the fundamental and shall be able to appear as discrete frequencies or as a wide-band spectrum.

- User shall be able to set a starting point anywhere in the waveform, assuming there will be enough sample points available after the starting point.

L.	Power meter shall provide sequence of events capture and recording.

1.	Meter shall have at least eight high-speed status inputs for capturing external events.

2.	All high-speed status inputs shall be monitored at a user set rate from 1 to 8 samples per millisecond.

3.	All changes in status shall be time stamped to the nearest millisecond and placed in an event log with time and event label information.

4.	Event log shall enable users to recreate sequence of events involving external status points.

5.	High-speed status inputs shall be able to trigger waveform recording to the waveform log.

6.	Status inputs shall be configurable for event monitoring, pulse accumulation, or pulse synchronizing.

M.	Power meter shall provide a separate IRIG-B input for time synchronizing to GPS time signal.

1.	IRIG-B input shall accept un-modulated time signal input from a standard GPS satellite clock.

2.	Time input shall enable time synchronizing to one millisecond and shall not be subject to network or other delays.

N.	Power meter shall provide an external display to accommodate access to readings locally and/or remotely.

- Display shall be a three line, LED format, P40N/P40N+ display.

- The meter shall be capable of providing readings to a P40N/P40N+, P41N, and P43N series of LED displays simultaneously.

- LED displays shall be 0.56-inch size and display shall include 10-character alphanumeric segment to provide legend and scaling information for displayed values.  The LED display shall use one communication port.

4.	Display shall connect to Power Meter via RS485 communications architecture. The communication channel shall be isolated at the display to avoid the introduction of noise.

5.	Display shall be able to be powered directly from Power Meter or from an auxiliary power supply.

6.	Display shall communicate with Power Meter using Modbus protocol.

7.	Display must be capable of operating over common communications channels. It shall be capable of being connected up to 5,000 feet from the Power Meter.

8.	Display shall be surface mounted for ease of installation.

9.	P40N+ display shall have a USB port to allow direct data downloads to a 			PC from the display.

O.	Power meter shall be equipped with non-volatile RAM for recording logs and programming information.

1.	Standard memory shall not be less than 4 MB.

2.	Meter shall store historical trending data, power quality data, and waveform recordings in memory.

3.	Memory shall be allocated to the various logging functions required. All logging features required shall be simultaneously available at the specified levels. Exercising any one feature at the specified level shall not limit exercising of any or all other features to their full, specified level.

4.	Meter shall store all programming and set-up parameters in non-volatile memory. In the event of loss of control power, meter programming data stored in memory shall be retained for at least 5 years.

P.	Power meter shall provide historical data logging for trending of measured values.

1.	Power meter shall contain two independent data logs.

2.	Each historical log shall be user configurable. User may select measured quantities and reading intervals for each log.

3.	Each historical log shall record at least 170 days of data where 5 readings are being stored every 15 minutes.

- One of the historical logs shall be configurable for time of use recording.

Q. 	 The monitor shall internally record and store Time of Use.

1.	The following Time of Use parameters must be included:

  - Twenty year calendar

  - Four seasons

  - Twelve Holidays per season

  - Four TOU schedules per season

  - Eight tariff registers

2.	The meter must display the following information in real-time when the TOU is enabled:

a.   Current month accumulations

- Previous month accumulations

- Current season accumulations

- Previous season accumulations

- Total accumulations to date

- Full four quadrant accumulations for Watt-hr, VAR-hr, VA-hr and coincident VARs during peak watt demand including max demand, shall be available for each tariff schedule, each season and for total accumulations.

R.	Power meter shall provide extensive power quality monitoring capability.

- Power meter shall measure and record the magnitude and phase angle of all real time harmonics through the 128th for all voltages and currents. Meter shall provide THD and K-Factor for all channels.

2.	All harmonic magnitude values shall be available through the digital communications ports in real time.

3.	Power meter shall capture and record all ITIC/CBEMA quality events.

4.	ITIC/CBEMA events shall be date/time stamped to the millisecond. Entries to CBEMA log shall include date/time stamp, duration, and magnitude information. The CBEMA log shall be downloadable through the digital communications ports.

5.	The CBEMA log shall hold over 1024 events in a revolving FIFO format.

6.	Power meter shall capture and record out-of-limit conditions in a log. Entries to Limits log shall be made anytime a monitored quantity exceeds the user set limit assigned to that quantity.

7.	Entries to the Limits log shall be time stamped to the millisecond and include the measured quantity value and label.

8.	The Limits log shall hold over 1024 events in a revolving FIFO format.

9.	The meter shall incorporate an interface to AI Reports Artificial 				Intelligence Reporting Software.

S.	Power meter shall provide waveform recording to capture and record transients and quality problems on current and voltage waveforms.

1.	Meter shall sample waveform at a user configurable rate of 16 to 512 samples per cycle (60Hz cycle).

2.	Meter shall hold at least 96 records of waveform recording in non-volatile memory. Each record shall be a minimum of 8 cycles in duration at the highest sample rate or 64 cycles in duration at the lowest sample rate.

3.	Each waveform record shall include pre-event and post-event data.

4.	Waveforms shall be recorded with time resolution to within one (1) millisecond.

5.	A waveform record shall be taken whenever the RMS value of voltage or current exceeds user-set limits.

6.	User shall be able to configure meter so that a waveform record shall be taken whenever a status change occurs on any one of the eight high-speed status inputs.

T.	Power meter shall have expandable auxiliary I/O capability.

1.	Meter shall allow connection of external I/O modules.

2.	Up to four (4) 8 channel external I/O modules shall be capable of being powered directly from the power meter. An auxiliary power supply shall be available to power additional I/O modules if needed.

3.	External I/O modules shall be isolated from the power meter and from each other.

4.	I/O modules shall connect to the power meter using RS485 communication architecture and shall be capable of being placed up to 5000 feet from the power meter.

5.	External I/O modules shall communicate with the power meter using Modbus protocol. Closed protocols shall not be accepted.

6.	External I/O modules shall include analog output modules that have four to eight channels each and shall allow the use of 0-1 mA outputs or 4-20 mA outputs; analog input modules that have 8 channels; digital pulse outputs; control relay outputs; and digital inputs.

7.	External I/O modules shall be able to be added to the meter after installation to provide upgrade capability after the initial installation is complete. Changing the power meter shall not be required to provide this upgrade capability.

U.	Power meter shall be programmable by software supplied by the meter manufacturer.

1.	Software shall include capacity to program meter, download meter, and 
analyze downloaded data files.

- Software shall store all data in an ODBC compliant database. Data based 
     storage shall include all log and waveform data.

V.	Meter shall offer ElectroLogic™ programmable logical protection and control.

1.	The 7000 values that the meter measures shall be programmable with 	limits and logic that trigger operations.

2.	The programmable logic structure shall allow users to develop up to three 	levels of logic control based on limits and status conditions.

3.	The logic structure shall be programmable through a graphical tree 	structure, and shall allow the user to set logical descriptors such as:

a.	AND/NAND/XAND gates

b.	OR/NOR/XOR gates

c.	Hysteresis/NHysteresis control

4.	The graphical programming structure shall be easily configurable to the 	user’s desired logical scheme.

5.	The control function shall be extendible to at least sixteen relay outputs.

W.	Power meter shall be appropriately constructed to provide long life in abusive physical and electrical environments.

1.	Meter shall be housed in an all-metal enclosure with no visible openings and no exposed circuit boards.

2.	Meter shall operate successfully at temperature extremes from –30 oC to +70 oC.

3.	Meter shall be UL listed.

4.	Meter shall operate with control power from 90 to 276 Volts AC/DC; meter shall have a power supply option to operate with control power of 18 to 60 Volts DC.

- Meter shall have a standard 4-year warranty.

X.	Power meter shall be Electro Industries / Gaugetech model: Nexus® 1252 meter.

- Approved model number is EIG Nexus 1252-D2-P40N.

2.	Order option –G for 600 Volt phase-to-phase direct connection. Do not specify this option if meter is to be used with potential transformers.

3.	Approved I/O modules and options list:

a.	INP2 – 56K with Dial-Out

b.	INP200 – 10/100BaseT Ethernet with Total Web Solutions

c.	1mAON4 – 4 analog outputs, 0-1mA

d.	1mAON8 – 8 analog outputs, 0-1mA

e.	20mAON4 – 4 analog outputs, 4-20mA

f.	20mAON8 – 8 analog outputs, 4-20mA

g.	4RO1 – 4 relay outputs

h.	4PO1 – 4 solid state pulse outputs

  - 8AI1 - 8 analog inputs, 0-1mA, scalable and bi-directional

  - 8AI2 - 8 analog inputs, 0-20mA, scalable.

  - 8AI3 - 8 analog inputs, 0-5VDC

  - 8AI4 - 8 analog inputs, 0-10VDC

  - 8DI1 - 8 digital status inputs, wet/dry auto-detect, up to 300V 	AC/DC

  - MBIO – Output Module Mounting Bracket (must be ordered with   	purchase of Output Module)

  - PSI0 – Power Supply for additional 10 modules

  - COMEXT4P – Communicator EXT, professional version

4.	For specification information, contact Electro Industries/GaugeTech at:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

sales@electroind.com